## README
WindPACT 5.0 MW Reference Model
Summary
The WindPACT models are a series of scaled reference models that were originally created in the early 2000s to investigate the financial impacts of turbine scaling [1]. There are four models, each of different size: 0.75 MW, 1.5 MW, 3.0 MW, and 5.0 MW. This Excel design file contains the parameters necessary for the FAST v7 input files for the WindPACT 5.0 MW Reference Model. There is a sheet with an overview of the model, and the FAST v7 parameters are separated into 5 different sheets: AeroDyn, Blades, Control, Nacelle, and Tower. The file also contains three sheets with detailed calculations for the Blade, Tower, and Drivetrain structural properties.
Technical Details
The design file was originally made by D.J. Malcolm as part of the WindPACT Turbine Rotor Design study in 2000 [1] (0.75 model version A04V00). The file has been heavily edited by Jenni Rinker to remove extraneous/redundant information and to add parameters that were not included in the original design. Some of the added values were taken from FAST v7 CertTest model WP 1.5, which was created by Bonnie Jonkman based on the original WindPACT 1.5 Reference Model. The file is organized into sheets. The main sheet is the first one, titled "Model Summary", and it has an overview of the model parameters. The next five sheets are FAST 7 parameters that have been intentionally isolated to facilitate porting the model to FAST 7. The last three sheets contain the structural calculations done by Global Energy Concepts (GEC) as part of the original study. The overview sheet is to orient the designer, the five FAST sheets are to facilitate the creation of the FAST v7 input files, and the last three sheets are purely informative.
Usage
Users can take the FAST v7 parameters directly from the five FAST sheets, or change parameters in the tabs to modify the design. The design calculations can also be examined in the last three sheets of the file.
Contacts
For issues with this document, please contact Jenni Rinker at jennifer.m.rinker@gmail.com.
References
[1] Malcolm, D. & Hansen, A. WindPACT Turbine Rotor Design Study National Renewable Energy Laboratory, National Renewable Energy Laboratory, 2006

## Model Summary
Model Name | 5.0 MW | WindPACT 5.0 MW Reference Model Basic input values are in green, All other colors are dependents, JR: <text> is an edit by Jenni Rinker
Use the RED coord. system to define c.g. locations:
Part | c.g. locations (m) wrt nacelle coords |  |  |  | Mom. of inertia about each parts c.g. (kg-m^2)
Name | X | Y | Z | Mass (kg) | Ixx | Iyy | Izz
Mainframe | -0.078053 | 0 | -0.74355 | 212987.971 | 520409.9189 | 701969.1751 | 587873.5383
Gen. Shaft | 1.3878 | 0 | 0 | 6651.7161 | 11354296.8935 | 5238.4227 | 5238.4227
Rotor Shaft | -1.582 | 0 | 0 | 51029.022 | 11735.9034 | 146483.8444 | 146483.8444
Hub | -6 | 0 | 0 | 125969.6223 | 924035.5242 | 924035.5242 | 924035.5242
Hub height (m) | 154
Number of blades | 3
Tilt Angle (deg) | 5 | Positive tilt raises the hub
Up or down wind | up
Rotor diameter (m) | 128
Drivetrain torsional spring constant (N-m/radian) | 2300693019.9789 |  | <-- JR: fixed error in equation B14
Drivetrain damping (% critical) | 5 |  | <-- JR: assumed/added this for damper calculations
Rotor inertia (kg-m^2) | 64807728 |  | <-- JR: calculated this from a dummy FAST run, added for torsional damper calculations
Air Density (kg/m^3) | 1.225
coning angle (deg) | 0 | Positive coning moves the blade tip downwind. | [5 empty] | This drawing is for a down wind, clockwise machine. |  |  |  |  | This drawing is for a up wind, clockwise machine.
drive train efficiency for induction motor. Parameters A1 and A2 | 0.95 |  | <-- JR: changed GenEff defn from original 4-parameter model for induction generators
free or fixed yaw | fixed | [6 empty] | For the blade coords.- the X-axis is along the chord line for each blade segment and
Y is toward the trailing edge (I.e., left hand coord. System for pitching).
If induction generator: | [7 empty] | Blade is pitched zero degrees , coning is positive (Blade tip downwind).
Synch. rotor rpm | 11.1906 | [6 empty] | Drawing shows zero tilt. Positive tilt raises the hub.
% slip | 1 | [6 empty] | For the RED coord. system, X is downwind.
Rated Power (kW) | 5000
If variable speed generator:
Max. rotor rpm | 11.1906
Rated (low speed shaft) torque (N-m) | 4491228.0702
Rated (high speed shaft) torque (N-m) | 27921.9198
Pitch control data:
Min. pitch angle (deg) | 2.6
Max. pitch angle (deg) | 90
Max. pitch rate (deg/sec) | 10
Gain scheduling start pitch angle (deg) | 2.6 |  | <-- JR: taken from CertTest WP 1.5
Gain scheduling end pitch angle (deg) | 30 |  | <-- JR: taken from CertTest WP 1.5
Gain scheduling exponent | -0.5 |  | <-- JR: taken from CertTest WP 1.5
Time step (sec) | 0.025 |  | <-- JR: taken from CertTest WP 1.5
Torque control data:
Generator torque constant (HSS N-m/rpm^2) | 0.0086179 |  | <-- JR: calculated assuming no R2.5 (simple quadratic fit)
tower data
distance of twr top below hub ht (m) | 2.928
top diameter (m) | 4.41
top thickness (mm) | 16
base diameter (m) | 10.17
base thickness (mm) | 35.7
Parasitic weight increase (%) | 5
Tip/tower clearance
parked clearance (m) | 8.1828
Hub
Overall outer diameter | 6.4 | m | Initial value = 0.05*D
Blade root bolt diam | 3.594 | m | from blade design sheet (chord at 5% r/R). DG says this is correct (16oct00)
Shaft connection diam | 3.09 | m | Initially = 2*shaft OD
Wall thickness | 0.1 | m | Preliminary
Material density | 7850 | kg/m^3
CGx | -6 | m | Initial value = 0.05*D, will be - for upwind turbine
CGy | 0 | m
CGz | 0 | m
Mainshaft
Length | 3.6 | m | Initial value = 0.03*D (shorter than for 750 kW?)
Outside diam | 1.04 | m
Inside diam | 0.52 | m | Initially set equal to 0.5*outside diam
Material density | 7850 | kg/m^3
CGy | 0 | m | CGx is calculated as the average of the 2 bearing locations
CGz | 0 | m
Bearings
1st CGx | -4.2 | m | Initially .035*D, will be - for upwind turbine
1st CGy | 0 | m
1st CGz | 0 | m
2nd CGx | -1.2 | m | Initially .01*D, will be - for upwind turbine
2nd CGy | 0 | m
2nd CGz | 0 | m
Gearbox
Mass | 42259 | kg | Initially set to a value which satisfies 200000 hrs at rated*1.1
CGx | 0 | m | Initially set at 0
CGy | 0 | m
CGz | 0 | m
tip speed | 75 | m/s
max motor speed | 1800 | rpm
Ratio | 160.8495
Low Speed RPM | 11.1906 |  | tip speed = 65 m/s
Generator
Rating | 5000 | kW
CGx | 1.5 | m | Initially set equal to 0.0125*D, will be - for downwind turbine
CGy | 0 | m
CGz | 0 | m
Bedplate
Length | 4.2 | m | Length from 1st bearing to yaw CL
Critical section width | 4.5 | m | Critical section is at yaw CL
Critical section depth | 2.208 | m
Critical section base thickness | 0.391 | m
Critical section wall thickness | 0.353 | m
Material density | 7850 | m
CGx | 0 | m
CGy | 0 | m
CGz | -1.464 | m | Initially set to -1/2 dist from shaft to yaw bearing, = -.0122*D
Total masses
Rotor (blades + hub) | 209406.6176 | kg
Nacelle (total head - rotor) | 270668.7091 | kg
Total head | 480075.3267 | kg
total tower | 775097.1818 | kg
Blade Moment-strain relationships (green blocks copied from blade design speadsheet): | [6 empty] | Unit Moment-strain relationships:
|  | flap design mt |  |  | edge mt |  |  | eF,Comp | eF,Tens | eE
Station | yC (mm) | Mf (N m) | eF,C (me) | eF,T (me) | ME (N-m) | eE (me) | Station | (me/N-m) | (me/N-m) | (me/N-m)
7% | 1744.3134 | 29122938.2973 | 3620 | 3620 | 29122938.2973 | 3620 | 7% | 0.0001243 | 0.0001243 | 0.0001243
25% | 820.8394 | 18532000 | 3620 | 3831.1604 | 3703647.8899 | 975.9303 | 25% | 0.00019534 | 0.00020673 | 0.00026351
50% | 461.4693 | 7977800 | 3620 | 3770.5999 | 954719.9833 | 975.9303 | 50% | 0.00045376 | 0.00047264 | 0.0010222
75% | 280.1883 | 2056600 | 3620 | 3790.3939 | 332680.4993 | 975.9303 | 75% | 0.0017602 | 0.001843 | 0.0029335
Blade Structural Properties Block (green blocks copied from blade design speadsheet):
| Chord | Section | Spar Cap | Gen. Axis Loc. | CG Loc. | E. Axis Loc. | Unit Weight | EIFlap | EIEdge | EA | GJ | IZ
Station | (m) | (t/c) | (% t) | (y/c) | (y/c) | (y/c) | (kg/m) | (N-m2) | (N-m2) | (N) | (N-m2) | ([kg/m]-m2)
5% | 3.4564 | 1 | NA | 0.25 | 0.5 | 0.5 | 3708.4116 | 63720689411.7532 | 63720689411.7532 | 42582928810.7462 | 22057695577.5487 | 11076.0263
7% | 3.4564 | 1 | NA | 0.25 | 0.5 | 0.5 | 622.3232 | 14036801421.6347 | 14036801421.6347 | 9469182296.333 | 4904988079.2989 | 1858.7116
25% | 5.1199 | 0.33 | 4.4775 | 0.34 | 0.40156 | 0.32671 | 684.4005 | 4203286116.1719 | 12611588173.0541 | 9141425662.3435 | 145303921.8404 | 959.8345
50% | 3.9256 | 0.24 | 8.9762 | 0.31 | 0.37589 | 0.32336 | 516.2703 | 1017265797.3257 | 2540323261.1102 | 6898689157.7993 | 57861076.0916 | 304.4401
75% | 2.7313 | 0.21 | 8.8011 | 0.28 | 0.38746 | 0.32613 | 225.1572 | 159223885.5632 | 610414304.9756 | 2907294183.0128 | 11605234.2134 | 65.91
100% | 1.6566 | 0.16 | 0 | 0.25 | 0.4925 | 0.3578 | 21.9861 | 1559775.5372 | 53624369.6541 | 235713983.5936 | 1237516.5813 | 5.4492
| Ratio of mass moments of intertia, IX/IY = |  | (direct input) |  | JR: cylinder GenAxisLoc changed to produce correct AeroCent
Twist and Airfoil Schedule (direct input, zero twist at 75% span):
| Twist | Airfoil ID
Station | (deg)
5% | 10.5 |  | 1
7% | 10.5 |  | 1
25% | 10.5 |  | 2
50% | 2.5 |  | 2.5
75% | 0 |  | 3
100% | -0.6 |  | 4
Airfoil ID | Airfoil Filename
1 |  | cylinder.dat |  | <-- JR: added ".dat" to be consistent with automatic input file generation routines
2 |  | s818_2703.dat |  | <-- JR: changed to "sXXX_XX03.dat" as "XX02.dat" airfoil parameters could not be located
3 |  | s825_2103.dat |  | <-- JR: changed to "sXXX_XX03.dat" as "XX02.dat" airfoil parameters could not be located
4 |  | s826_1603.dat |  | <-- JR: changed to "sXXX_XX03.dat" as "XX02.dat" airfoil parameters could not be located
blade modal damping ratios |  |  |  | <-- JR: added blade modal damping ratios from CertTest WP 1.5
1st flap | 2nd flap | 1st edge
0.03882 | 0.03882 | 0.059
tower modal damping ratios |  |  |  | <-- JR: added tower modal damping ratios from CertTest WP 1.5
1st fore-aft | 0.03435
2nd fore-aft | 0.03435
1st side-side | 0.03435
2nd side-side | 0.03435
Mass properties:
Mainframe includes all non-rotating mass on top of tower
Gen. Shaft includes all high-speed shaft rotating mass
Rotor shaft includes all low-speed shaft rotating mass
Hub is all of rotor except the blades
None of the models will contain a gearbox. All mass and torque properties are referenced to the low-speed shaft values.
Log of Modifications
Oct 26 2000 Parasitic mass of tower added. Initial value = 10%
Dec 14 2000. Calculation of total masses added
Note: we are designing the tower base to have a zero margin, keeping the same ratiio of b/t (210:1). The tower top will be designed to have a zero margin or will be specified to have a minimum diameter of 0.5 times the base diameter (and the same b/t=210 ratio)
Note on B1: model name = # of megawatts, configuration letter (A-Z), revision #.

## FAST7_AeroDyn
Units | Key | Values
kg/m^3 | AirDens | 1.225
s | DTAero | 0.005
- | FoilNm | cylinder.dat | s818_2703.dat | s825_2103.dat | s826_1603.dat
- | BldNodes | 15
| ADSchedFields | RNodes | AeroTwst | DRNodes | Chord | NFoil | PrnElm
|  | 5.2267 | 11.1 | 4.0533 | 3.5643 | 1 | NOPRINT
|  | 9.28 | 11.1 | 4.0533 | 4.1495 | 2 | NOPRINT
|  | 13.3333 | 11.1 | 4.0533 | 4.7348 | 2 | NOPRINT
|  | 17.3867 | 10.4067 | 4.0533 | 5.0164 | 2 | NOPRINT
|  | 21.44 | 8.38 | 4.0533 | 4.7138 | 2 | NOPRINT
|  | 25.4933 | 6.3533 | 4.0533 | 4.4113 | 2 | NOPRINT
|  | 29.5467 | 4.3267 | 4.0533 | 4.1087 | 2 | NOPRINT
|  | 33.6 | 2.85 | 4.0533 | 3.8061 | 3 | NOPRINT
|  | 37.6533 | 2.2167 | 4.0533 | 3.5036 | 3 | NOPRINT
|  | 41.7067 | 1.5833 | 4.0533 | 3.201 | 3 | NOPRINT
|  | 45.76 | 0.95 | 4.0533 | 2.8985 | 3 | NOPRINT
|  | 49.8133 | 0.532 | 4.0533 | 2.6095 | 3 | NOPRINT
|  | 53.8667 | 0.38 | 4.0533 | 2.3372 | 3 | NOPRINT
|  | 57.92 | 0.228 | 4.0533 | 2.065 | 4 | NOPRINT
|  | 61.9733 | 0.076 | 4.0533 | 1.7927 | 4 | NOPRINT
| ADSched Calculations |  |  | Chord | Twist | Airfoil
| 0.5 | 0.033333 | 3.2 | 3.4564 | 11.1 | 1
| 1.5 | 0.1 | 4.48 | 3.4564 | 11.1 | 1
| 2.5 | 0.16667 | 16 | 5.1199 | 11.1 | 2
| 3.5 | 0.23333 | 32 | 3.9256 | 3.1 | 2.5
| 4.5 | 0.3 | 48 | 2.7313 | 0.6 | 3
| 5.5 | 0.36667 | 64 | 1.6566 | 0 | 4
| 6.5 | 0.43333
| 7.5 | 0.5
| 8.5 | 0.56667
| 9.5 | 0.63333
| 10.5 | 0.7
| 11.5 | 0.76667
| 12.5 | 0.83333
| 13.5 | 0.9
| 14.5 | 0.96667

## FAST7_Blades
Units | Key | Values
m | BldFlDmp(1) | 3.882 | [7 empty] | RotorDiameter
m | BldFlDmp(2) | 3.882 | [7 empty] | HubDiameter
% | BldEdDmp(1) | 5.9 | [7 empty] | BladeDamping (%)
| DistBldProps | BlFract | AeroCent | StrcTwst | BMassDen | FlpStff | EdgStff | GJStff | EAStff | BladeSchedule
|  | 0 | 0.25 | 11.1 | 3708.4116 | 63720689411.7532 | 63720689411.7532 | 22057695577.5487 | 42582928810.7462
|  | 0.021053 | 0.25 | 11.1 | 622.3232 | 14036801421.6347 | 14036801421.6347 | 4904988079.2989 | 9469182296.333
|  | 0.052632 | 0.22943 | 11.1 | 632.6694 | 12397882204.0575 | 13799265880.2046 | 4111707386.3891 | 9414556190.6681
|  | 0.10526 | 0.20119 | 11.1 | 649.9131 | 9666350174.7623 | 13403373311.1544 | 2789572898.2062 | 9323512681.2266
|  | 0.15789 | 0.17855 | 11.1 | 667.1568 | 6934818145.4671 | 13007480742.1042 | 1467438410.0233 | 9232469171.7851
|  | 0.21053 | 0.16 | 11.1 | 684.4005 | 4203286116.1719 | 12611588173.0541 | 145303921.8404 | 9141425662.3435
|  | 0.26316 | 0.16483 | 9.5 | 650.7745 | 3566082052.4027 | 10597335190.6653 | 127815352.6906 | 8692878361.4347
|  | 0.31579 | 0.17015 | 7.9 | 617.1484 | 2928877988.6334 | 8583082208.2765 | 110326783.5408 | 8244331060.5259
|  | 0.36842 | 0.17605 | 6.3 | 583.5224 | 2291673924.8642 | 6568829225.8877 | 92838214.3911 | 7795783759.617
|  | 0.42105 | 0.18262 | 4.7 | 549.8963 | 1654469861.095 | 4554576243.499 | 75349645.2413 | 7347236458.7082
|  | 0.47368 | 0.19 | 3.1 | 516.2703 | 1017265797.3257 | 2540323261.1102 | 57861076.0916 | 6898689157.7993
|  | 0.52632 | 0.19445 | 2.6 | 458.0477 | 845657414.9732 | 2154341469.8833 | 48609907.7159 | 6100410162.842
|  | 0.57895 | 0.19951 | 2.1 | 399.8251 | 674049032.6207 | 1768359678.6563 | 39358739.3403 | 5302131167.8847
|  | 0.63158 | 0.20532 | 1.6 | 341.6024 | 502440650.2682 | 1382377887.4294 | 30107570.9647 | 4503852172.9274
|  | 0.68421 | 0.21207 | 1.1 | 283.3798 | 330832267.9157 | 996396096.2025 | 20856402.5891 | 3705573177.9701
|  | 0.73684 | 0.22 | 0.6 | 225.1572 | 159223885.5632 | 610414304.9756 | 11605234.2134 | 2907294183.0128
|  | 0.78947 | 0.22395 | 0.48 | 184.523 | 127691063.558 | 499056317.9113 | 9531690.687 | 2372978143.1289
|  | 0.84211 | 0.22864 | 0.36 | 143.8888 | 96158241.5528 | 387698330.847 | 7458147.1606 | 1838662103.2451
|  | 0.89474 | 0.23429 | 0.24 | 103.2545 | 64625419.5476 | 276340343.7827 | 5384603.6342 | 1304346063.3612
|  | 0.94737 | 0.24124 | 0.12 | 62.6203 | 33092597.5424 | 164982356.7184 | 3311060.1078 | 770030023.4774
|  | 1 | 0.25 | 0 | 21.9861 | 1559775.5372 | 53624369.6541 | 1237516.5813 | 235713983.5936

## FAST7_Control
Units | Key | Values
rpm | VS_RtGnSp | 1800
N-m | VS_RtTq | 27921.9198
N-m/HSSrpm^2 | VS_Rgn2K | 0.0086179
deg | BlPitchF(1) | 2.6
deg | BlPitchF(2) | 2.6
deg | BlPitchF(3) | 2.6
rpm | CNST(2) | 11.1906 |  |  | rotor speed set point
deg | CNST(4) | 2.6 |  |  | min pitch angle
deg | CNST(5) | 90 |  |  | max pitch angle
s | CNST(6) | 0.025 |  |  | pitch time step
rad | CNST(7) | 0.045379 |  |  | gain scheduling start angle
rad | CNST(8) | 0.5236 |  |  | gain scheduling end angle
- | CNST(9) | 0.21302 |  |  | gain scheduling coefficient
- | CNST(10) | -0.5 |  |  | gain scheduling exponent
| P2P_Num | 21.9727 | 0 | 0 | numerator blade pitch actuator TF
| P2P_Den | 21.9727 | 7.5 | 1 | denominator blade pitch actuator TF

## FAST7_Nacelle
Units | Key | Values
m | OverHang | -6
m | NacCMxn | -0.32557
m | NacCMyn | 0
m | NacCMzn | 2.3429
m | TowerHt | 151.072
m | Twr2Shft | 2.928
deg | ShftTilt | -5
deg | PreCone(1) | 0
deg | PreCone(2) | 0
deg | PreCone(3) | 0
kg | NacMass | 270668.7091
kg | HubMass | 125969.6223
kg-m^2 | NacYIner | 739595.8054
kg-m^2 | GenIner | 438.8545
kg-m^2 | HubIner | 668484.9701
- | GenEff | 95
- | GBRatio | 160.8495
N-m/rad | DTTorSpr | 2300693019.9789
N-m/(rad/s) | DTTorDmp | 14909175.1811
W | RatedPwr | 5000000
m | TipRad | 64
m | HubRad | 3.2

## FAST7_Tower
Units | Key | Values
% | TwrFADmp(1) | 3.435
| TwrFADmp(2) | 3.435
| TwrSSDmp(1) | 3.435
| TwrSSDmp(2) | 3.435
| TwrSchedFields | HtFract | TMassDen | TwFAStif | TwSSStif | TwGJStif | TwEAStif
|  | 0 | 9401.5183 | 2.9493e+12 | 2.9493e+12 | 2.2687e+12 | 228122980629.2385
|  | 0.11111 | 8269.7153 | 2.278e+12 | 2.278e+12 | 1.7523e+12 | 200660364475.4479
|  | 0.22222 | 7210.4631 | 1.7284e+12 | 1.7284e+12 | 1.3295e+12 | 174958157218.3889
|  | 0.33333 | 6223.7617 | 1.2848e+12 | 1.2848e+12 | 988322204305.4617 | 151016358858.0614
|  | 0.44444 | 5309.6112 | 932637953883.6528 | 932637953883.6528 | 717413810679.7329 | 128834969394.4654
|  | 0.55556 | 4468.0115 | 658356143729.3505 | 658356143729.3505 | 506427802868.7311 | 108413988827.601
|  | 0.66667 | 3698.9627 | 449540087092.6099 | 449540087092.6099 | 345800066994.3153 | 89753417157.4682
|  | 0.77778 | 3002.4647 | 294838031157.999 | 294838031157.999 | 226798485506.153 | 72853254384.067
|  | 0.88889 | 2378.5176 | 183979818336.2375 | 183979818336.2375 | 141522937181.7212 | 57713500507.3973
|  | 1 | 1827.1214 | 107776886264.1973 | 107776886264.1973 | 82905297126.3056 | 44334155527.4592

## BladeCalculations
Initial Properties (transferred from blade design spreadsheet via Main page):
| Chord | Section | Spar Cap | Gen. Axis Loc. | CG Loc. | E. Axis Loc. | Unit Weight | EIFlap | EIEdge | EA | GJ | IZ
Station | (m) | (t/c) | (% t) | (y/c) | (y/c) | (y/c) | (kg/m) | (N-m2) | (N-m2) | (N) | (N-m2) | ([kg/m]-m2)
5% | 3.4564 | 1 | NA | 0.25 | 0.5 | 0.5 | 3708.4116 | 63720689411.7532 | 63720689411.7532 | 42582928810.7462 | 22057695577.5487 | 11076.0263
7% | 3.4564 | 1 | NA | 0.25 | 0.5 | 0.5 | 622.3232 | 14036801421.6347 | 14036801421.6347 | 9469182296.333 | 4904988079.2989 | 1858.7116
25% | 5.1199 | 0.33 | 4.4775 | 0.34 | 0.40156 | 0.32671 | 684.4005 | 4203286116.1719 | 12611588173.0541 | 9141425662.3435 | 145303921.8404 | 959.8345
50% | 3.9256 | 0.24 | 8.9762 | 0.31 | 0.37589 | 0.32336 | 516.2703 | 1017265797.3257 | 2540323261.1102 | 6898689157.7993 | 57861076.0916 | 304.4401
75% | 2.7313 | 0.21 | 8.8011 | 0.28 | 0.38746 | 0.32613 | 225.1572 | 159223885.5632 | 610414304.9756 | 2907294183.0128 | 11605234.2134 | 65.91
100% | 1.6566 | 0.16 | 0 | 0.25 | 0.4925 | 0.3578 | 21.9861 | 1559775.5372 | 53624369.6541 | 235713983.5936 | 1237516.5813 | 5.4492
| Rotor radius = | 64 | m
| Hub radius = | 3.2 | m
Shifted and adjusted properties
Station | Length | Mass | IX | IY | CG Offset | CG Offset | E.A. Offset | E.A. Offset | Twist | GJ | EA | EIEdge | EIFlap | Chord | A. C. Offset | Airfoil
(% R) | z/L | (kg/m) | ([kg/m]-m2) | ([kg/m]-m2) | X (m) | Y (m) | X (m) | Y (m) | (deg.) | (N-m2) | (N) | (N-m2) | (N-m2) | (m) | (m) | Filename
5% | 0 | 3708.4116 | 0 | 11076.0263 | 0 | 0.86411 | 0 | 0.86411 | 11.1 | 22057695577.5487 | 42582928810.7462 | 63720689411.7532 | 63720689411.7532 | 3.4564 | 0 | 1
7% | 0.021053 | 622.3232 | 0 | 1858.7116 | 0 | 0.86411 | 0 | 0.86411 | 11.1 | 4904988079.2989 | 9469182296.333 | 14036801421.6347 | 14036801421.6347 | 3.4564 | 0 | 1
25% | 0.21053 | 684.4005 | 0 | 959.8345 | 0 | 0.31518 | 0 | -0.068028 | 11.1 | 145303921.8404 | 9141425662.3435 | 12611588173.0541 | 4203286116.1719 | 5.1199 | -0.46079 | 2
50% | 0.47368 | 516.2703 | 0 | 304.4401 | 0 | 0.25865 | 0 | 0.052458 | 3.1 | 57861076.0916 | 6898689157.7993 | 2540323261.1102 | 1017265797.3257 | 3.9256 | -0.23553
75% | 0.73684 | 225.1572 | 0 | 65.91 | 0 | 0.2935 | 0 | 0.126 | 0.6 | 11605234.2134 | 2907294183.0128 | 610414304.9756 | 159223885.5632 | 2.7313 | -0.081938 | 3
100% | 1 | 21.9861 | 0 | 5.4492 | 0 | 0.40172 | 0 | 0.17858 | 0 | 1237516.5813 | 235713983.5936 | 53624369.6541 | 1559775.5372 | 1.6566 | 0 | 4
Interpolated Properties:
Station | Length | Mass | IX | IY | CG Offset | CG Offset | E.A. Offset | E.A. Offset | Twist | GJ | EA | EIEdge | EIFlap | Chord | A. C. Offset | Airfoil | total mass
(% R) | z/L | (kg/m) | ([kg/m]-m2) | ([kg/m]-m2) | X (m) | Y (m) | X (m) | Y (m) | (deg.) | (N-m2) | (N) | (N-m2) | (N-m2) | (m) | (m) | Filename
5% | 0 | 3708.4116 | 0 | 11076.0263 | 0 | 0.86411 | 0 | 0.86411 | 11.1 | 22057695577.5487 | 42582928810.7462 | 63720689411.7532 | 63720689411.7532 | 3.4564 | 0 | 1 | 2373.3835
7% | 0.021053 | 622.3232 | 0 | 1858.7116 | 0 | 0.86411 | 0 | 0.86411 | 11.1 | 4904988079.2989 | 9469182296.333 | 14036801421.6347 | 14036801421.6347 | 3.4564 | 0 | 1 | 995.7171
10% | 0.052632 | 632.6694 | 0 | 1708.8988 | 0 | 0.77262 | 0 | 0.70875 | 11.1 | 4111707386.3891 | 9414556190.6681 | 13799265880.2046 | 12397882204.0575 | 3.7337 | -0.076798 | 1 | 1619.6337
15% | 0.10526 | 649.9131 | 0 | 1459.2107 | 0 | 0.62014 | 0 | 0.44983 | 11.1 | 2789572898.2062 | 9323512681.2266 | 13403373311.1544 | 9666350174.7623 | 4.1957 | -0.2048 | 2 | 2079.722
20% | 0.15789 | 667.1568 | 0 | 1209.5226 | 0 | 0.46766 | 0 | 0.1909 | 11.1 | 1467438410.0233 | 9232469171.7851 | 13007480742.1042 | 6934818145.4671 | 4.6578 | -0.33279 | 2 | 2134.9018
25% | 0.21053 | 684.4005 | 0 | 959.8345 | 0 | 0.31518 | 0 | -0.068028 | 11.1 | 145303921.8404 | 9141425662.3435 | 12611588173.0541 | 4203286116.1719 | 5.1199 | -0.46079 | 2 | 2190.0817
30% | 0.26316 | 650.7745 | 0 | 828.7556 | 0 | 0.30387 | 0 | -0.043931 | 9.5 | 127815352.6906 | 8692878361.4347 | 10597335190.6653 | 3566082052.4027 | 4.881 | -0.41574 | 2 | 2082.4784
35% | 0.31579 | 617.1484 | 0 | 697.6768 | 0 | 0.29257 | 0 | -0.019834 | 7.9 | 110326783.5408 | 8244331060.5259 | 8583082208.2765 | 2928877988.6334 | 4.6422 | -0.37069 | 2 | 1974.875
40% | 0.36842 | 583.5224 | 0 | 566.5979 | 0 | 0.28126 | 0 | 0.0042634 | 6.3 | 92838214.3911 | 7795783759.617 | 6568829225.8877 | 2291673924.8642 | 4.4033 | -0.32564 | 2 | 1867.2716
45% | 0.42105 | 549.8963 | 0 | 435.519 | 0 | 0.26996 | 0 | 0.02836 | 4.7 | 75349645.2413 | 7347236458.7082 | 4554576243.499 | 1654469861.095 | 4.1644 | -0.28059 | 2 | 1759.6683
50% | 0.47368 | 516.2703 | 0 | 304.4401 | 0 | 0.25865 | 0 | 0.052458 | 3.1 | 57861076.0916 | 6898689157.7993 | 2540323261.1102 | 1017265797.3257 | 3.9256 | -0.23553 | 2 | 1652.0649
55% | 0.52632 | 458.0477 | 0 | 256.7341 | 0 | 0.26562 | 0 | 0.067166 | 2.6 | 48609907.7159 | 6100410162.842 | 2154341469.8833 | 845657414.9732 | 3.6867 | -0.20482 | 3 | 1465.7526
60% | 0.57895 | 399.8251 | 0 | 209.0281 | 0 | 0.27259 | 0 | 0.081875 | 2.1 | 39358739.3403 | 5302131167.8847 | 1768359678.6563 | 674049032.6207 | 3.4479 | -0.1741 | 3 | 1279.4402
65% | 0.63158 | 341.6024 | 0 | 161.3221 | 0 | 0.27956 | 0 | 0.096583 | 1.6 | 30107570.9647 | 4503852172.9274 | 1382377887.4294 | 502440650.2682 | 3.209 | -0.14338 | 3 | 1093.1278
70% | 0.68421 | 283.3798 | 0 | 113.616 | 0 | 0.28653 | 0 | 0.11129 | 1.1 | 20856402.5891 | 3705573177.9701 | 996396096.2025 | 330832267.9157 | 2.9701 | -0.11266 | 3 | 906.8154
75% | 0.73684 | 225.1572 | 0 | 65.91 | 0 | 0.2935 | 0 | 0.126 | 0.6 | 11605234.2134 | 2907294183.0128 | 610414304.9756 | 159223885.5632 | 2.7313 | -0.081938 | 3 | 720.5031
80% | 0.78947 | 184.523 | 0 | 53.8178 | 0 | 0.31514 | 0 | 0.13652 | 0.48 | 9531690.687 | 2372978143.1289 | 499056317.9113 | 127691063.558 | 2.5163 | -0.06555 | 3 | 590.4735
85% | 0.84211 | 143.8888 | 0 | 41.7257 | 0 | 0.33679 | 0 | 0.14703 | 0.36 | 7458147.1606 | 1838662103.2451 | 387698330.847 | 96158241.5528 | 2.3014 | -0.049163 | 3 | 460.444
90% | 0.89474 | 103.2545 | 0 | 29.6335 | 0 | 0.35843 | 0 | 0.15755 | 0.24 | 5384603.6342 | 1304346063.3612 | 276340343.7827 | 64625419.5476 | 2.0865 | -0.032775 | 4 | 330.4145
95% | 0.94737 | 62.6203 | 0 | 17.5414 | 0 | 0.38008 | 0 | 0.16806 | 0.12 | 3311060.1078 | 770030023.4774 | 164982356.7184 | 33092597.5424 | 1.8715 | -0.016388 | 4 | 200.385
100% | 1 | 21.9861 | 0 | 5.4492 | 0 | 0.40172 | 0 | 0.17858 | 0 | 1237516.5813 | 235713983.5936 | 53624369.6541 | 1559775.5372 | 1.6566 | 0 | 4 | 35.1777
27812.3317

## TowerCalculations
tower coordinates:
z = vertical
x = downwind
y = lateral
hub height= | 154 | m | steel density= | 7850 | kg/m^3
yaw brg ht= | 151.072 | m | steel modulus= | 200000000000 | N/m^2
base diam = | 10.17 | m | steel G= | 76923076923.0769 | N/m^2
top diam = | 4.41 | m
base thickness= | 35.7 | mm
top thickness= | 16 | mm
parasitic mass= | 5 | %
station | height\m | diam | thickness | area | mass/length | EA | Izz | mass Izz | GJ | Iyy, Ixx | mass Iyy,Ixx | Eiyy=Eixx | total mass
| m | m | mm | m^2 | kg/m | N | m^4 | kg m^2/m | N m^2 | m^4 | kg m^2/m | N m^2 | kg
0 | 0 | 10.17 | 35.7 | 1.1406 | 9401.5183 | 228122980629.2385 | 29.4931 | 231521.1191 | 2.2687e+12 | 14.7466 | 115760.5595 | 2.9493e+12 | 78905.8988
1 | 16.7858 | 9.53 | 33.5111 | 1.0033 | 8269.7153 | 200660364475.4479 | 22.7802 | 178824.5199 | 1.7523e+12 | 11.3901 | 89412.26 | 2.278e+12 | 138813.6028
2 | 33.5716 | 8.89 | 31.3222 | 0.87479 | 7210.4631 | 174958157218.3889 | 17.2841 | 135680.485 | 1.3295e+12 | 8.6421 | 67840.2425 | 1.7284e+12 | 121033.2305
3 | 50.3573 | 8.25 | 29.1333 | 0.75508 | 6223.7617 | 151016358858.0614 | 12.8482 | 100858.2809 | 988322204305.4617 | 6.4241 | 50429.1405 | 1.2848e+12 | 104470.6807
4 | 67.1431 | 7.61 | 26.9444 | 0.64417 | 5309.6112 | 128834969394.4654 | 9.3264 | 73212.0794 | 717413810679.7329 | 4.6632 | 36606.0397 | 932637953883.6528 | 89125.9533
5 | 83.9289 | 6.97 | 24.7556 | 0.54207 | 4468.0115 | 108413988827.601 | 6.5836 | 51680.9573 | 506427802868.7311 | 3.2918 | 25840.4786 | 658356143729.3505 | 74999.0484
6 | 100.7147 | 6.33 | 22.5667 | 0.44877 | 3698.9627 | 89753417157.4682 | 4.4954 | 35288.8968 | 345800066994.3153 | 2.2477 | 17644.4484 | 449540087092.6099 | 62089.966
7 | 117.5004 | 5.69 | 20.3778 | 0.36427 | 3002.4647 | 72853254384.067 | 2.9484 | 23144.7854 | 226798485506.153 | 1.4742 | 11572.3927 | 294838031157.999 | 50398.706
8 | 134.2862 | 5.05 | 18.1889 | 0.28857 | 2378.5176 | 57713500507.3973 | 1.8398 | 14442.4157 | 141522937181.7212 | 0.9199 | 7221.2079 | 183979818336.2375 | 39925.2685
9 | 151.072 | 4.41 | 16 | 0.22167 | 1827.1214 | 44334155527.4592 | 1.0778 | 8460.4856 | 82905297126.3056 | 0.53888 | 4230.2428 | 107776886264.1973 | 15334.8268
775097.1818

## DrivetrainCalculations
Rotor diameter, m: | 128
Generator rpm | 1800
Rotating components | Length, m | Inside Diameter, m | Outside Diameter, m | Wall thickness, m |  | Density, kg/m^3 | Mass, kg | CGx, m | CGy, m | CGz, m | Ix about cg, kg.m^2 | Iy about cg, kg.m^2 | Iz about cg, kg.m^2 | mrx^2 kg.m^2 | mry^2 kg.m^2 | mrz^2 kg.m^2
Hub |  |  | 6.4 | 0.1 |  | 7850 | 101013.5135 | -6 | 0 | 0 | 668484.9701 | 668484.9701 | 668484.9701 | 0 | 7.9686e-26 | 7.9686e-26 | Hub
Pitch bearings (all n blds) | [6 empty] | 24956.1088 | -6 | 0 | 0 | 255550.5541 | 255550.5541 | 255550.5541 | 0 | 1.9687e-26 | 1.9687e-26 | Hub
Mainshaft | 3.6 | 0.52 | 1.04 |  |  | 7850 | 18004.8696 | -2.7 | 0 | 0 | 3042.823 | 20966.6707 | 20966.6707 | 0 | 22504.0902 | 22504.0902 | LSS
1st bearing |  | 1.04 |  |  |  |  | 5947.3262 | -4.2 | 0 | 0 | 1608.157 | 804.0785 | 804.0785 | 0 | 40762.0357 | 40762.0357 | LSS
2nd bearing |  | 1.04 |  |  |  |  | 5947.3262 | -1.2 | 0 | 0 | 1608.157 | 804.0785 | 804.0785 | 0 | 867.9286 | 867.9286 | LSS
Gearbox (rotating, 1/2 total) | 1.536 |  | 1.44 |  |  |  | 21129.5 | 0 | 0 | 0 | 5476.7664 | 6892.6119 | 6892.6119 | 0 | 52882.3504 | 52882.3504 | LSS
Generator rotor (1/3 total) | 3.072 | [5 empty] | 5657 | 1.5 | 0 | 0 | 8402084.3541 | 4611.2202 | 4611.2202 | 0 | 71.1606 | 71.1606 | HSS
HSS,cpling,brk disk | 0.025 |  | 1.56 |  |  | 7850 | 994.7161 | 0.75 | 0 | 0 | 2952212.5394 | 151.3481 | 151.3481 | 0 | 404.6939 | 404.6939 | HSS
[11 empty] | Ix total | Iy total | Iz total
[6 empty] | Hub subtotal | 125969.6223 | -6 | 0 | 0 | 924035.5242 | 924035.5242 | 924035.5242
[6 empty] | LSS subtotal | 51029.022 | -1.582 | 0 | 0 | 11735.9034 | 146483.8444 | 146483.8444
[6 empty] | HSS subtotal | 6651.7161 | 1.3878 | 0 | 0 | 11354296.8935 | 5238.4227 | 5238.4227
[6 empty] | Drive train subtotal | 183650.3604 | -4.5048 | 0 | 0
Bedplate only
Non-rotating components | Length, m | Critical section width, m | Critical section depth, m | C sect base thickness, m | C sect wall thickness, m
Bedplate | 4.2 | 4.5 | 2.208 | 0.391 | 0.353 | 7850 | 108174.8127 | 0 | 0 | -1.464 | 339740.0908 | 328887.02 | 328887.02 | 56147.4153 | 56806.4465 | 659.0313
1st bearing hsng |  |  | 1.56 |  |  |  | 6221.3635 | -4.2 | 0 | 0 | 3785.0776 | 1892.5388 | 1892.5388 | 3439.6154 | 109143.3596 | 105703.7443
2nd bearing hsng |  |  | 1.56 |  |  |  | 6221.3635 | -1.2 | 0 | 0 | 3785.0776 | 1892.5388 | 1892.5388 | 3439.6154 | 11270.8496 | 7831.2342
Gearbox hsng (1/2 total) | 1.536 | 1.44 | 1.92 |  |  |  | 21129.5 | 0 | 0 | 0 | 15213.24 | 11760.8487 | 11760.8487 | 11681.9011 | 11810.6279 | 128.7268
Generator hsng (2/3 total) | 3.072 | 0.96 | 1.92 |  |  |  | 11314 | 1.5 | 0 | 0 | 6516.864 | 12156.1236 | 12156.1236 | 6255.1896 | 34429.8946 | 28174.705
Nacelle cover | 8.4 | 2.208 | 4.5 |  |  |  | 11868.192 | 0 | 0 | 0 | 37273.9322 | 88421.935 | 88421.935 | 6561.5866 | 6633.891 | 72.3044
Other ME | [6 empty] | 44664.5394 | 0 | 0 | 0 | 0 | 0 | 0 | 24693.7566 | 24965.8655 | 272.1089
Other EE | [6 empty] | 3394.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1876.5569 | 1897.2353 | 20.6784
[11 empty] | Ix total | Iy total | Iz total
[6 empty] | Nacelle subtotal | 212987.971 | -0.078053 | 0 | -0.74355 | 520409.9189 | 701969.1751 | 587873.5383
[6 empty] | Tower head total less blades | 396638.3315 | -2.1277 | 0 | -0.39928
Notes for calculated quantities
Hub - Mass | pi*t*p*od^2
Hub - Ix,y,z | .4*mass*(r^5-(r-t)^5)/(r^3-(r-t)^3)
Pitch Bngs - CG | Use hub cg since pitch brng properties will add to overall hub properties
Pitch Bngs - Mass | 0.0119*Rotor Diam^3 Ref D. Malcolm kickoff mtg presentation
Pitch Bngs - Ix,y,z | mass*r^2 about the hub cg , with hub radius
Shaft - mass | density*volume
Shaft - CGx | average of main bearing cg's
Shaft - Ix,y,z | Ix=mass*(od^2+id^2)/8 Iy,z=mass*(od^2+id^2+(4/3)*l^2)/16
Bearings - ID | =mainshaft OD
Bearings - mass | .00002613*ID^2.77 where ID is in mm
Bearings - Ix,y,z | Ix=mass*r^2 Iy,Iz=Ix/2 where r = ID/2
Gearbox rotating - length | 0.012*rotor diameter est. from various drawings and experience
Gearbox rotating - OD | housing ID
Gearbox rotating - mass | 1/2 of total gearbox mass
Gearbox - rotating Ix,y,z | Assume a solid cylinder, Ix=(md^2)/8, Iy,z=m(0.75*d^2+l^2)/12
Generator rotating - length | 0.024*rotor diameter est. from various drawings and experience
Generator rotating - mass | (3.3*rating+471)/3 Ref S.U. '94 1/3 for rotor
Generator rotating - Ix | 48.6e-6*rotor diamter^5.333 i.e. aero rotor, ref T. McCoy 9/22/00 N4 notebook, includes gear ratio^2
Generator rotating - Iy,z | Ix/2/gear ratio^2 + (ml^2)/12
HSS,cplng,brk disk - length | For brk disk only, thickness in x direction, set =1 inch
HSS,cplng,brk disk - OD | For brk disk only, OD=1.5*mainshaft OD
HSS,cplng,brk disk - mass | From S.U. '94 1.5*.025*1000*rating/gen RPM in radians
HSS,cplng,brk disk - CG | average of gen and gbox cg's
HSS,cplng,brk disk - Ix,y,z | brk disk only, solid cylinder, calc mass form disk dimensions and density
Bedplate - mass | 1.5*p*(0.00000042875*D^3-(0.00030625*t+0.00003675*W+0.0000735*d)*D^2+(0.035*tW+0.07*td)*D)
Bedplate - Ix,y,z | Assume a hollow cylinder and use width as OD and depth as ID
Brng hsngs - OD | 1.5*ID
Brng hsngs - mass | 67.44e-6*ID^2.64 where ID is in mm
Brng hsngs - Ix,y,z | Ix=mass*r^2 , Iy,z=Ix/2 where r = ID/2
Gearbox hsng - length | 0.012*rotor diameter est. from various drawings and experience
Gearbox hsng - OD | 0.015*rotor diameter est. from various drawings and experience
Gearbox hsng - ID | 0.75*OD
Gearbox hsng - mass | 1/2 of total gearbox mass
Gearbox hsng - Ix,y,z | Assume a hollow cylinder, Ix=m*(ID^2+OD^2)/8, Iy,z=Ix/2+m(l^2)/12
Generator hsng - length | 0.024*rotor diameter est. from various drawings and experience
Generator hsng - OD | 0.015*rotor diameter est. from various drawings and experience
Generator hsng - ID | 0.5*OD
Generator hsng - mass | 2/3 of total mass
Generator hsng - Ix,y,z | Assume a hollow cylinder, Ix=m*(ID^2+OD^2)/8, Iy,z=Ix/2+m(l^2)/12
Nacelle cover - length | 2*bedplate (upwind) length
Nacelle cover - ID | set equal to bedplate depth
Nacelle cover - OD | set equal to bedplate width
Nacelle cover - mass | From SU '94 84.1*(2*L^2)
Nacelle cover - Ix,y,z | Assume a hollow cylinder, Ix=m*(ID^2+OD^2)/8, Iy,z=Ix/2+m(l^2)/12
Other ME | From SU '94, mass of lube, hydr, other=2.6*rating mass of yaw sys=.002168*rotor diam^3.4, curve fit of SU results, CG=0, no inertia calculated
Other EE | 20% of gen mass, in nacelle, CG=0, no inertia calculated
All - mr^2 | Ix = mass*((z-zcg)^2+(y-ycg)^2)